{"text_format":"3","workbook":"xls","n_sheets":3,"sheets":["Sheet1","Sheet2","Sheet3"],"not_rendered":{"external_links":1,"defined_names":1},"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Sheet1","index":0,"n_rows":56,"n_cols":13,"rows_kept":56,"merged":[[0,0,0,12],[1,0,1,12],[2,0,4,0],[2,1,4,1],[2,2,4,2],[2,3,4,3],[2,11,4,11],[2,12,4,12]],"flags":["formulas_cached_only"]}
["01上半月管网水半月检常规项目检验汇总表"]
["委托单位名称：淄博市自来水有限责任公司                                                                               检测单位：淄博安瑞水质检测有限责任公司                                                                                                                                                                                                                                                                                               "]
["序号","采样日期","采样地点","样品编号","菌落总数","总大肠菌群","色度","浑浊度","臭和味","二氧化氯","高锰酸盐指数（以O2计）","报告日期","检测人员"]
[{"$nulls":4},"CFU/mL","CFU/100mL","度","NTU","/","mg/L","mg/L"]
[{"$nulls":4},"≤100","不应检出","≤15","≤1","无异臭、异味","出厂水和末梢水中限值0.8，出厂水中余量≥0.1，末梢水中余量 ≥0.02","≤3"]
[1,"2026.01.19","淄博市政务中心","20260119-0051",5,"未检出","<5","0.21","无",0.04,"/","2026.01.21"," 王晓芳"]
[2,"2026.01.19","车站街道办事处","20260119-0052",7,"未检出","<5","0.24","无",0.05,"/","2026.01.21"," 王晓芳"]
[3,"2026.01.19","王舍生活二区","20260119-0053",8,"未检出","<5","0.26","无",0.03,1.35,"2026.01.21"," 王晓芳"]
[4,"2026.01.19","石家社区","20260119-0054",3,"未检出","<5","0.23","无",0.04,"/","2026.01.21"," 王晓芳"]
[5,"2026.01.19","福源汇社区","20260119-0055",7,"未检出","<5","0.22","无",0.05,"/","2026.01.21"," 王晓芳"]
[6,"2026.01.19","通济花园社区","20260119-0056",11,"未检出","<5","0.24","无",0.05,"/","2026.01.21"," 王晓芳"]
[7,"2026.01.20","淄博市委","20260120-0057",9,"未检出","<5","0.31","无",0.05,"/","2026.01.22"," 王晓芳"]
[8,"2026.01.20","五里桥生活区","20260120-0058",6,"未检出","<5","0.25","无",0.04,"/","2026.01.22"," 王晓芳"]
[9,"2026.01.20","于小社区","20260120-0059",3,"未检出","<5","0.23","无",0.04,"/","2026.01.22"," 王晓芳"]
[10,"2026.01.20","碧桂园社区","20260120-0060",5,"未检出","<5","0.26","无",0.05,"/","2026.01.22"," 王晓芳"]
[11,"2026.01.20","孝妇河湿地公园","20260120-0061",7,"未检出","<5","0.27","无",0.03,1.44,"2026.01.22"," 王晓芳"]
[12,"2026.01.20","福瑞家园社区","20260120-0062",8,"未检出","<5","0.20","无",0.04,1.38,"2026.01.22"," 王晓芳"]
[13,"2026.01.20","盛世康城社区","20260120-0063",11,"未检出","<5","0.22","无",0.03,"/","2026.01.22"," 王晓芳"]
[14,"2026.01.21","黄金国际社区","20260121-0064",5,"未检出","<5","0.30","无",0.05,"/","2026.01.23"," 王晓芳"]
[15,"2026.01.21","市自来水公司新区营业所","20260121-0065",9,"未检出","<5","0.25","无",0.03,"/","2026.01.23"," 王晓芳"]
[16,"2026.01.21","颐丰花园社区","20260121-0066",5,"未检出","<5","0.27","无",0.04,"/","2026.01.23"," 王晓芳"]
[17,"2026.01.21","世纪花园社区","20260121-0067",7,"未检出","<5","0.31","无",0.05,1.41,"2026.01.23"," 王晓芳"]
[18,"2026.01.21","瑞丰苑社区","20260121-0068","未检出","未检出","<5","0.28","无",0.05,"/","2026.01.23"," 王晓芳"]
[19,"2026.01.21","科技苑社区","20260121-0069",19,"未检出","<5","0.23","无",0.04,"/","2026.01.23"," 王晓芳"]
[20,"2026.01.22","山泉路70号","20260122-0070",3,"未检出","<5","0.20","无",0.05,"/","2026.01.24"," 王晓芳"]
[21,"2026.01.22","四砂社区","20260122-0071",8,"未检出","<5","0.29","无",0.04,1.29,"2026.01.24"," 王晓芳"]
[22,"2026.01.22","经开区后南定村","20260122-0072",5,"未检出","<5","0.28","无",0.05,"/","2026.01.24"," 王晓芳"]
[23,"2026.01.22","苹果园社区","20260122-0073",17,"未检出","<5","0.34","无",0.04,1.31,"2026.01.24"," 王晓芳"]
[24,"2026.01.22","五公里社区","20260122-0074",7,"未检出","<5","0.24","无",0.05,"/","2026.01.24"," 王晓芳"]
[25,"2026.01.22","张南路101号","20260122-0075",4,"未检出","<5",0.22,"无",0.04,"/","2026.01.24"," 王晓芳"]
[26,"2026.01.26","北苑社区","20260126-0076","未检出","未检出","<5","0.33","无",0.04,"/","2026.01.28"," 王晓芳"]
[27,"2026.01.26","金都花园社区","20260126-0077",1,"未检出","<5","0.20","无",0.03,1.43,"2026.01.28"," 王晓芳"]
[28,"2026.01.26","丁庄社区","20260126-0078",4,"未检出","<5","0.21","无",0.06,"/","2026.01.28"," 王晓芳"]
[29,"2026.01.26","外商居住区","20260126-0079",7,"未检出","<5","0.19","无",0.03,"/","2026.01.28"," 王晓芳"]
[30,"2026.01.26","华侨城社区","20260126-0080",41,"未检出","<5","0.34","无",0.02,"/","2026.01.28"," 王晓芳"]
[31,"2026.01.26","高新区高科技创业园","20260126-0081",19,"未检出","<5","0.23","无",0.04,"/","2026.01.28"," 王晓芳"]
[32,"2026.01.27","淄博市自来水公司宿舍区","20260127-0082",2,"未检出","<5","0.24","无",0.07,"/","2026.01.29"," 王晓芳"]
[33,"2026.01.27","行政执法局湖田中队","20260127-0083",10,"未检出","<5","0.28","无",0.03,"/","2026.01.29"," 王晓芳"]
[34,"2026.01.27","洪三社区","20260127-0084",4,"未检出","<5","0.21","无",0.04,"/","2026.01.29"," 王晓芳"]
[35,"2026.01.27","西张社区","20260127-0085",6,"未检出","<5","0.30","无",0.06,1.33,"2026.01.29"," 王晓芳"]
[36,"2026.01.27","恒嘉园社区","20260127-0086",8,"未检出","<5","0.29","无",0.04,"/","2026.01.29"," 王晓芳"]
[37,"2026.01.27","金乔社区","20260127-0087","未检出","未检出","<5","0.18","无",0.05,1.32,"2026.01.29"," 王晓芳"]
[38,"2026.01.27","潘庄社区","20260127-0088","未检出","未检出","<5","0.17","无",0.06,"/","2026.01.29"," 王晓芳"]
[39,"2026.01.28","四宝山街道办事处","20260128-0089",4,"未检出","<5","0.20","无",0.07,"/","2026.01.30"," 王晓芳"]
[40,"2026.01.28","淄博市十一中","20260128-0090",2,"未检出","<5","0.19","无",0.05,"/","2026.01.30"," 王晓芳"]
[41,"2026.01.28","大张社区","20260128-0091",6,"未检出","<5","0.22","无",0.04,1.28,"2026.01.30"," 王晓芳"]
[42,"2026.01.28","齐悦国际社区","20260128-0092",3,"未检出","<5","0.32","无",0.03,"/","2026.01.30"," 王晓芳"]
[43,"2026.01.28","凯瑞溪园社区","20260128-0093",7,"未检出","<5","0.22","无",0.06,"/","2026.01.30"," 王晓芳"]
[44,"2026.01.29","北西五路5号院","20260129-0094",6,"未检出","<5","0.32","无",0.05,"/","2026.01.31"," 王晓芳"]
[45,"2026.01.29","祥瑞花园社区","20260129-0095",3,"未检出","<5","0.28","无",0.04,"/","2026.01.31"," 王晓芳"]
[46,"2026.01.29","张店八中","20260129-0096",4,"未检出","<5","0.26","无",0.03,"/","2026.01.31"," 王晓芳"]
[47,"2026.01.29","积家村社区","20260129-0097",21,"未检出","<5","0.31","无",0.05,1.35,"2026.01.31"," 王晓芳"]
[48,"2026.01.29","明德苑社区","20260129-0098",5,"未检出","<5","0.22","无",0.04,1.22,"2026.01.31"," 王晓芳"]
[49,"2026.01.29","花漾城社区","20260129-0099",1,"未检出","<5","0.25","无",0.05,"/","2026.01.31"," 王晓芳"]
[50,"2026.01.29","淄博市档案馆","20260129-0100",11,"未检出","<5","0.23","无",0.03,"/","2026.01.31"," 王晓芳"]
[null,null,"以下空白"]

{"sheet":"Sheet2","index":1,"n_rows":0,"n_cols":0,"rows_kept":0,"flags":["formulas_cached_only"]}

{"sheet":"Sheet3","index":2,"n_rows":0,"n_cols":0,"rows_kept":0,"flags":["formulas_cached_only"]}