{"text_format":"3","workbook":"xls","n_sheets":3,"sheets":["Sheet1","Sheet2","Sheet3"],"not_rendered":{"external_links":1,"defined_names":1},"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Sheet1","index":0,"n_rows":56,"n_cols":13,"rows_kept":56,"merged":[[0,0,0,12],[1,0,1,12],[2,0,4,0],[2,1,4,1],[2,2,4,2],[2,3,4,3],[2,11,4,11],[2,12,4,12]],"flags":["formulas_cached_only"]}
["01上半月管网水半月检常规项目检验汇总表"]
["委托单位名称：淄博市自来水有限责任公司                                                                               检测单位：淄博安瑞水质检测有限责任公司                                                                                                                                                                                                                                                                                               "]
["序号","采样日期","采样地点","样品编号","菌落总数","总大肠菌群","色度","浑浊度","臭和味","二氧化氯","高锰酸盐指数（以O2计）","报告日期","检测人员"]
[{"$nulls":4},"CFU/mL","CFU/100mL","度","NTU","/","mg/L","mg/L"]
[{"$nulls":4},"≤100","不应检出","≤15","≤1","无异臭、异味","出厂水和末梢水中限值0.8，出厂水中余量≥0.1，末梢水中余量 ≥0.02","≤3"]
[1,"2026.01.04","淄博市政务中心","20260104-0001",1,"未检出","<5",0.19,"无",0.05,"/","2026.01.06"," 王晓芳"]
[2,"2026.01.04","车站街道办事处","20260104-0002",5,"未检出","<5",0.22,"无",0.04,"/","2026.01.06"," 王晓芳"]
[3,"2026.01.04","王舍生活二区","20260104-0003",3,"未检出","<5",0.24,"无",0.04,1.33,"2026.01.06"," 王晓芳"]
[4,"2026.01.04","石家社区","20260104-0004",9,"未检出","<5",0.25,"无",0.03,"/","2026.01.06"," 王晓芳"]
[5,"2026.01.04","福源汇社区","20260104-0005",1,"未检出","<5",0.21,"无",0.04,"/","2026.01.06"," 王晓芳"]
[6,"2026.01.04","通济花园社区","20260104-0006",15,"未检出","<5",0.25,"无",0.03,"/","2026.01.06"," 王晓芳"]
[7,"2026.01.06","淄博市委","20260106-0007",3,"未检出","<5",{"v":0.3,"d":"0.30"},"无",0.04,"/","2026.01.08"," 王晓芳"]
[8,"2026.01.06","五里桥生活区","20260106-0008",1,"未检出","<5",0.23,"无",0.03,"/","2026.01.08"," 王晓芳"]
[9,"2026.01.06","于小社区","20260106-0009",7,"未检出","<5",0.25,"无",0.05,"/","2026.01.08"," 王晓芳"]
[10,"2026.01.06","碧桂园社区","20260106-0010",11,"未检出","<5",0.27,"无",0.06,"/","2026.01.08"," 王晓芳"]
[11,"2026.01.06","孝妇河湿地公园","20260106-0011",5,"未检出","<5",0.29,"无",0.04,1.47,"2026.01.08"," 王晓芳"]
[12,"2026.01.06","福瑞家园社区","20260106-0012",4,"未检出","<5",0.18,"无",0.03,1.41,"2026.01.08"," 王晓芳"]
[13,"2026.01.06","盛世康城社区","20260106-0013",9,"未检出","<5",{"v":0.2,"d":"0.20"},"无",0.04,"/","2026.01.08"," 王晓芳"]
[14,"2026.01.07","黄金国际社区","20260107-0014",13,"未检出","<5",0.28,"无",0.04,"/","2026.01.09"," 王晓芳"]
[15,"2026.01.07","市自来水公司新区营业所","20260107-0015",6,"未检出","<5",0.23,"无",0.04,"/","2026.01.09"," 王晓芳"]
[16,"2026.01.07","颐丰花园社区","20260107-0016",11,"未检出","<5",{"v":0.3,"d":"0.30"},"无",0.05,"/","2026.01.09"," 王晓芳"]
[17,"2026.01.07","世纪花园社区","20260107-0017",15,"未检出","<5",{"v":0.3,"d":"0.30"},"无",0.03,1.45,"2026.01.09"," 王晓芳"]
[18,"2026.01.07","瑞丰苑社区","20260107-0018",1,"未检出","<5",0.26,"无",0.03,"/","2026.01.09"," 王晓芳"]
[19,"2026.01.07","科技苑社区","20260107-0019",8,"未检出","<5",0.22,"无",0.04,"/","2026.01.09"," 王晓芳"]
[20,"2026.01.08","山泉路70号","20260108-0020",6,"未检出","<5",0.19,"无",0.04,"/","2026.01.10"," 王晓芳"]
[21,"2026.01.08","四砂社区","20260108-0021",11,"未检出","<5",0.27,"无",0.03,1.32,"2026.01.10"," 王晓芳"]
[22,"2026.01.08","经开区后南定村","20260108-0022",3,"未检出","<5",0.26,"无",0.04,"/","2026.01.10"," 王晓芳"]
[23,"2026.01.08","苹果园社区","20260108-0023",21,"未检出","<5",0.36,"无",0.05,1.27,"2026.01.10"," 王晓芳"]
[24,"2026.01.08","五公里社区","20260108-0024",12,"未检出","<5",0.23,"无",0.04,"/","2026.01.10"," 王晓芳"]
[25,"2026.01.08","张南路101号","20260108-0025",1,"未检出","<5",0.21,"无",0.05,"/","2026.01.10"," 王晓芳"]
[26,"2026.01.12","北苑社区","20260112-0026",9,"未检出","<5",0.34,"无",0.03,"/","2026.01.14"," 王晓芳"]
[27,"2026.01.12","金都花园社区","20260112-0027","未检出","未检出","<5",0.19,"无",0.04,{"v":1.4,"d":"1.40"},"2026.01.14"," 王晓芳"]
[28,"2026.01.12","丁庄社区","20260112-0028",2,"未检出","<5",0.22,"无",0.05,"/","2026.01.14"," 王晓芳"]
[29,"2026.01.12","外商居住区","20260112-0029",3,"未检出","<5",0.17,"无",0.02,"/","2026.01.14"," 王晓芳"]
[30,"2026.01.12","华侨城社区","20260112-0030",30,"未检出","<5",0.33,"无",0.03,"/","2026.01.14"," 王晓芳"]
[31,"2026.01.12","高新区高科技创业园","20260112-0031",11,"未检出","<5",0.21,"无",0.03,"/","2026.01.14"," 王晓芳"]
[32,"2026.01.13","淄博市自来水公司宿舍区","20260113-0032",5,"未检出","<5",0.22,"无",0.06,"/","2026.01.15"," 王晓芳"]
[33,"2026.01.13","行政执法局湖田中队","20260113-0033",3,"未检出","<5",{"v":0.3,"d":"0.30"},"无",0.02,"/","2026.01.15"," 王晓芳"]
[34,"2026.01.13","洪三社区","20260113-0034",1,"未检出","<5",0.23,"无",0.03,"/","2026.01.15"," 王晓芳"]
[35,"2026.01.13","西张社区","20260113-0035",2,"未检出","<5",0.32,"无",0.05,1.36,"2026.01.15"," 王晓芳"]
[36,"2026.01.13","恒嘉园社区","20260113-0036",4,"未检出","<5",{"v":0.3,"d":"0.30"},"无",0.05,"/","2026.01.15"," 王晓芳"]
[37,"2026.01.13","金乔社区","20260113-0037",5,"未检出","<5",{"v":0.2,"d":"0.20"},"无",0.06,1.35,"2026.01.15"," 王晓芳"]
[38,"2026.01.13","潘庄社区","20260113-0038",2,"未检出","<5",0.19,"无",0.05,"/","2026.01.15"," 王晓芳"]
[39,"2026.01.14","四宝山街道办事处","20260114-0039",2,"未检出","<5",0.22,"无",0.06,"/","2026.01.16"," 王晓芳"]
[40,"2026.01.14","淄博市十一中","20260114-0040","未检出","未检出","<5",0.18,"无",0.03,"/","2026.01.16"," 王晓芳"]
[41,"2026.01.14","大张社区","20260114-0041",2,"未检出","<5",0.21,"无",0.03,{"v":1.3,"d":"1.30"},"2026.01.16"," 王晓芳"]
[42,"2026.01.14","齐悦国际社区","20260114-0042",1,"未检出","<5",{"v":0.3,"d":"0.30"},"无",0.02,"/","2026.01.16"," 王晓芳"]
[43,"2026.01.14","凯瑞溪园社区","20260114-0043",3,"未检出","<5",0.24,"无",0.07,"/","2026.01.16"," 王晓芳"]
[44,"2026.01.15","北西五路5号院","20260115-0044",1,"未检出","<5",0.35,"无",0.06,"/","2026.01.17"," 王晓芳"]
[45,"2026.01.15","祥瑞花园社区","20260115-0045","未检出","未检出","<5",0.26,"无",0.05,"/","2026.01.17"," 王晓芳"]
[46,"2026.01.15","张店八中","20260115-0046",1,"未检出","<5",0.24,"无",0.04,"/","2026.01.17"," 王晓芳"]
[47,"2026.01.15","积家村社区","20260115-0047",10,"未检出","<5",{"v":0.3,"d":"0.30"},"无",0.03,1.25,"2026.01.17"," 王晓芳"]
[48,"2026.01.15","明德苑社区","20260115-0048","未检出","未检出","<5",0.21,"无",0.03,1.14,"2026.01.17"," 王晓芳"]
[49,"2026.01.15","花漾城社区","20260115-0049","未检出","未检出","<5",0.27,"无",0.06,"/","2026.01.17"," 王晓芳"]
[50,"2026.01.15","淄博市档案馆","20260115-0050",5,"未检出","<5",0.22,"无",0.04,"/","2026.01.17"," 王晓芳"]
[null,null,"以下空白"]

{"sheet":"Sheet2","index":1,"n_rows":0,"n_cols":0,"rows_kept":0,"flags":["formulas_cached_only"]}

{"sheet":"Sheet3","index":2,"n_rows":0,"n_cols":0,"rows_kept":0,"flags":["formulas_cached_only"]}